## Sheet1
DWG | signal_name | LOCATION | DESCRIPTION | HMI_Tag | PLC_Address | HMI_Screen | IO_TYPE | SYS_PNL_TAG | MDL_1 | RACK | POS | CHANNEL | MDL_PN | MDL1_PIN1 | MDL1_PIN2
PCS-AI.dwg | TK25_FD_01 | TANK #25 | Flame detector, Triple IR, 90 degree cone of vision, 35 meter min distance | TK25_FD_01 |  |  | AI |  |  | 1 | 8 | CH01
PCS-AI.dwg | TK25_FD_02 | TANK #25 | Flame detector, Triple IR, 90 degree cone of vision, 35 meter min distance . | TK25_FD_02 |  |  | AI |  |  | 1 | 8 | CH02
PCS-AI.dwg | TK24_FD_01 | TANK #24 | Flame detector, Triple IR, 90 degree cone of vision, 35 meter min distance. | TK24_FD_01 |  |  | AI |  |  | 1 | 8 | CH03
PCS-AI.dwg | TK24_FD_02 | TANK #24 | Flame detector, Triple IR, 90 degree cone of vision, 35 meter min distance. | TK24_FD_02 |  |  | AI |  |  | 1 | 8 | CH04
PCS-AI.dwg | TK23_FD_01 | TANK #23 | Flame detector, Triple IR, 90 degree cone of vision, 35 meter min distance . | TK23_FD_01 |  |  | AI |  |  | 1 | 8 | CH05
PCS-AI.dwg | TK23_FD_02 | TANK #23 | Flame detector, Triple IR, 90 degree cone of vision, 35 meter min distance. | TK23_FD_02 |  |  | AI |  |  | 1 | 8 | CH06
PCS-AI.dwg | TK25_GD_01 | TANK #25 | Spot Type Flammable Gas Detector, IR Sensor. | TK25_GD_01 |  |  | AI |  |  | 1 | 8 | CH07
PCS-AI.dwg | TK24_GD_01 | TANK #24 | Spot Type Flammable Gas Detector, IR Sensor. | TK24_GD_01 |  |  | AI |  |  | 1 | 8 | CH08
PCS-AI.dwg | TK24_GD_02 | TANK #24 | Spot Type Flammable Gas Detector, IR Sensor. | TK24_GD_02 |  |  | AI |  |  | 1 | 8 | CH09
PCS-AI.dwg | TK23_GD_01 | TANK #23 | Spot Type Flammable Gas Detector, IR Sensor. | TK23_GD_01 |  |  | AI |  |  | 1 | 8 | CH10
PCS-AI.dwg | TK23_GD_02 | TANK #23 | Spot Type Flammable Gas Detector, IR Sensor.Gas Boot (425_V_003), | TK23_GD_02 |  |  | AI |  |  | 1 | 8 | CH11
PCS-AI.dwg | LA_100 |  | Level Indicator Transmitter to initiate HH and LL Alarms | LA_100 |  |  | AI |  |  | 1 | 8 | CH12
PCS-AI.dwg | LA_101 | Process Tank (425_TK_024) | Process Tank (425_TK_024), Level Indicator Transmitter to initiate HH and LL Alarms | LA_101 |  |  | AI |  |  | 1 | 8 | CH13
PCS-AI.dwg | LA_102 | Process Tank (425_TK_024) | Process Tank (425_TK_023), Level Indicator Transmitter to initiate HH and LL Alarms | LA_102 |  |  | AI |  |  | 1 | 8 | CH14
PCS-AI.dwg | LA_103 | Process Tank (425_TK_024) | Process Tank (425_TK_023), Level Indicator Transmitter to initiate HH and LL Alarms | LA_103 |  |  | AI |  |  | 1 | 8 | CH15
PCS-AI - Copy.dwg | SPARE_AI00016 |  | SPARE | SPARE_AI00016 |  |  | AI |  |  | 1 | 8 | CH16
PCS-AI - Copy.dwg | SPARE_AI0017 |  | SPARE | SPARE_AI0017 |  |  | AI |  |  | 1 | 9 | CH01
PCS-AI - Copy.dwg | SPARE_AI0018 |  | SPARE | SPARE_AI0018 |  |  | AI |  |  | 1 | 9 | CH02
PCS-AI - Copy.dwg | SPARE_AI0019 |  | SPARE | SPARE_AI0019 |  |  | AI |  |  | 1 | 9 | CH03
PCS-AI - Copy.dwg | SPARE_AI0020 |  | SPARE | SPARE_AI0020 |  |  | AI |  |  | 1 | 9 | CH04
PCS-AI-Spare.dwg | SPARE_AI0021 |  | SPARE | SPARE_AI0021 |  |  | AI |  |  | 1 | 9 | CH05
PCS-AI-Spare.dwg | SPARE_AI0022 |  | SPARE | SPARE_AI0022 |  |  | AI |  |  | 1 | 9 | CH06
PCS-AI-Spare.dwg | SPARE_AI0023 |  | SPARE | SPARE_AI0023 |  |  | AI |  |  | 1 | 9 | CH07
PCS-AI-Spare.dwg | SPARE_AI0024 |  | SPARE | SPARE_AI0024 |  |  | AI |  |  | 1 | 9 | CH08
PCS-AI-Spare.dwg | SPARE_AI0025 |  | SPARE | SPARE_AI0025 |  |  | AI |  |  | 1 | 9 | CH09
PCS-AI-Spare.dwg | SPARE_AI0026 |  | SPARE | SPARE_AI0026 |  |  | AI |  |  | 1 | 9 | CH10
PCS-AI-Spare.dwg | SPARE_AI0027 |  | SPARE | SPARE_AI0027 |  |  | AI |  |  | 1 | 9 | CH11
PCS-AI-Spare.dwg | SPARE_AI0028 |  | SPARE | SPARE_AI0028 |  |  | AI |  |  | 1 | 9 | CH12
PCS-AI-Spare.dwg | SPARE_AI0029 |  | SPARE | SPARE_AI0029 |  |  | AI |  |  | 1 | 9 | CH13
PCS-AI-Spare.dwg | SPARE_AI0030 |  | SPARE | SPARE_AI0030 |  |  | AI |  |  | 1 | 9 | CH14
PCS-AI-Spare.dwg | SPARE_AI0031 |  | SPARE | SPARE_AI0031 |  |  | AI |  |  | 1 | 10 | CH15
PCS-AI-Spare.dwg | SPARE_AI0032 |  | SPARE | SPARE_AI0032 |  |  | AI |  |  | 1 | 10 | CH16
PCS-AI-Spare.dwg | SPARE_AI0033 |  | SPARE | SPARE_AI0033 |  |  | AI |  |  | 1 | 10 | CH01
PCS-AI-Spare.dwg | SPARE_AI0034 |  | SPARE | SPARE_AI0034 |  |  | AI |  |  | 1 | 10 | CH02
PCS-AI-Spare.dwg | SPARE_AI0035 |  | SPARE | SPARE_AI0035 |  |  | AI |  |  | 1 | 10 | CH03
PCS-AI-Spare.dwg | SPARE_AI0036 |  | SPARE | SPARE_AI0036 |  |  | AI |  |  | 1 | 10 | CH04
PCS-AI-Spare.dwg | SPARE_AI0037 |  | SPARE | SPARE_AI0037 |  |  | AI |  |  | 1 | 10 | CH05
PCS-AI-Spare.dwg | SPARE_AI0038 |  | SPARE | SPARE_AI0038 |  |  | AI |  |  | 1 | 10 | CH06
PCS-AI-Spare.dwg | SPARE_AI0039 |  | SPARE | SPARE_AI0039 |  |  | AI |  |  | 1 | 10 | CH07
PCS-AI-Spare.dwg | SPARE_AI0040 |  | SPARE | SPARE_AI0040 |  |  | AI |  |  | 1 | 10 | CH08
PCS-AI-Spare.dwg | SPARE_AI0041 |  | SPARE | SPARE_AI0041 |  |  | AI |  |  | 1 | 10 | CH09
PCS-AI-Spare.dwg | SPARE_AI0042 |  | SPARE | SPARE_AI0042 |  |  | AI |  |  | 1 | 10 | CH10
PCS-AI-Spare.dwg | SPARE_AI0043 |  | SPARE | SPARE_AI0043 |  |  | AI |  |  | 1 | 10 | CH11
PCS-AI-Spare.dwg | SPARE_AI0044 |  | SPARE | SPARE_AI0044 |  |  | AI |  |  | 1 | 10 | CH12
PCS-AI-Spare.dwg | SPARE_AI0045 |  | SPARE | SPARE_AI0045 |  |  | AI |  |  | 1 | 10 | CH13
PCS-AI-Spare.dwg | SPARE_AI0046 |  | SPARE | SPARE_AI0046 |  |  | AI |  |  | 1 | 10 | CH14
PCS-AI-Spare.dwg | SPARE_AI0047 |  | SPARE | SPARE_AI0047 |  |  | AI |  |  | 1 | 10 | CH15
PCS-AI-Spare.dwg | SPARE_AI0048 |  | SPARE | SPARE_AI0048 |  |  | AI |  |  | 1 | 10 | CH16
PCS-DO-Spare.dwg | SPARE_AQ0001 |  | SPARE_AQ0001 | SPARE_AQ0001 |  |  | AO |  |  | 1 | 11 | CH01
PCS-DO-Spare.dwg | SPARE_AQ0002 |  | SPARE_AQ0002 | SPARE_AQ0002 |  |  | AO |  |  | 1 | 11 | CH02
PCS-DO-Spare.dwg | SPARE_AQ0003 |  | SPARE_AQ0003 | SPARE_AQ0003 |  |  | AO |  |  | 1 | 11 | CH03
PCS-DO-Spare.dwg | SPARE_AQ0004 |  | SPARE_AQ0004 | SPARE_AQ0004 |  |  | AO |  |  | 1 | 11 | CH04
PCS-DO-Spare.dwg | SPARE_AQ0005 |  | SPARE_AQ0005 | SPARE_AQ0005 |  |  | AO |  |  | 1 | 11 | CH05
PCS-DO-Spare.dwg | SPARE_AQ0006 |  | SPARE_AQ0006 | SPARE_AQ0006 |  |  | AO |  |  | 1 | 11 | CH06
PCS-DO-Spare.dwg | SPARE_AQ0007 |  | SPARE_AQ0007 | SPARE_AQ0007 |  |  | AO |  |  | 1 | 11 | CH07
PCS-DO-Spare.dwg | SPARE_AQ0008 |  | SPARE_AQ0008 | SPARE_AQ0008 |  |  | AO |  |  | 1 | 11 | CH08
PCS-DO-Spare.dwg | SPARE_AQ0009 |  | SPARE_AQ0009 | SPARE_AQ0009 |  |  | AO |  |  | 1 | 12 | CH01
PCS-DO-Spare.dwg | SPARE_AQ0010 |  | SPARE_AQ0010 | SPARE_AQ0010 |  |  | AO |  |  | 1 | 12 | CH02
PCS-DO-Spare.dwg | SPARE_AQ0011 |  | SPARE_AQ0011 | SPARE_AQ0011 |  |  | AO |  |  | 1 | 12 | CH03
PCS-DO-Spare.dwg | SPARE_AQ0012 |  | SPARE_AQ0012 | SPARE_AQ0012 |  |  | AO |  |  | 1 | 12 | CH04
PCS-DO-Spare.dwg | SPARE_AQ0013 |  | SPARE_AQ0013 | SPARE_AQ0013 |  |  | AO |  |  | 1 | 12 | CH05
PCS-DO-Spare.dwg | SPARE_AQ0014 |  | SPARE_AQ0014 | SPARE_AQ0014 |  |  | AO |  |  | 1 | 12 | CH06
PCS-DO-Spare.dwg | SPARE_AQ0015 |  | SPARE_AQ0015 | SPARE_AQ0015 |  |  | AO |  |  | 1 | 12 | CH07
PCS-DO-Spare.dwg | SPARE_AQ0016 |  | SPARE_AQ0016 | SPARE_AQ0016 |  |  | AO |  |  | 1 | 12 | CH08
PCS-DI.dwg | RS_MCP_01 | TANK#25 | Manual Pull Station, Double Action | RS_MCP_01 |  |  | DI |  |  | 1 | 3 | CH01
PCS-DI.dwg | RS_MCP_02 | TANK#24 | Manual Pull Station, Double Action | RS_MCP_02 |  |  | DI |  |  | 1 | 3 | CH02
PCS-DI.dwg | RS_MCP_03 | NEW GAS BOOT | Manual Pull Station, Double Action | RS_MCP_03 |  |  | DI |  |  | 1 | 3 | CH03
PCS-DI.dwg | TK23_LHD_01 | TANK#23 | Linear Heat Detector, Setting Temperature (88) Celsius, For (TK_23) | TK23_LHD_01 |  |  | DI |  |  | 1 | 3 | CH04
PCS-DI.dwg | TK23_LHD_02 | TANK#23 | Linear Heat Detector, Setting Temperature (105) Celsius, For (TK_23) | TK23_LHD_02 |  |  | DI |  |  | 1 | 3 | CH05
PCS-DI.dwg | TK24_LHD_01 | TANK#24 | Linear Heat Detector, Setting Temperature (88) Celsius, For (TK_24) | TK24_LHD_01 |  |  | DI |  |  | 1 | 3 | CH06
PCS-DI.dwg | TK24_LHD_02 | TANK#24 | Linear Heat Detector, Setting Temperature (105) Celsius, For (TK_24) | TK24_LHD_02 |  |  | DI |  |  | 1 | 3 | CH07
PCS-DI.dwg | TK25_LHD_01 | TANK#25 | Linear Heat Detector, Setting Temperature (88) Celsius, For (TK_25) | TK25_LHD_01 |  |  | DI |  |  | 1 | 3 | CH08
PCS-DI.dwg | TK25_LHD_02 | TANK#25 | Linear Heat Detector, Setting Temperature (105) Celsius, For (TK_25) | TK25_LHD_02 |  |  | DI |  |  | 1 | 3 | CH09
PCS-DI.dwg | GB_LHD_01 | NEW GAS BOOT | Linear Heat Detector, Setting Temperature (88) Celsius, For (Gas Boot) | GB_LHD_01 |  |  | DI |  |  | 1 | 3 | CH10
PCS-DI.dwg | GB_LHD_02 | NEW GAS BOOT | Linear Heat Detector, Setting Temperature (105) Celsius, For (Gas Boot) | GB_LHD_02 |  |  | DI |  |  | 1 | 3 | CH11
PCS-DI.dwg | PSH_001 |  | Monitoring Signal of Pressure Switch of Tank 23 Cooling Deluge Valve | PSH_001 |  |  | DI |  |  | 1 | 3 | CH12
PCS-DI.dwg | PSH_002 |  | Monitoring Signal of Pressure Switch of Tank 23 Foam Deluge Valve | PSH_002 |  |  | DI |  |  | 1 | 3 | CH13
PCS-DI.dwg | PSH_003 |  | Monitoring Signal of Pressure Switch of Tank 24 Cooling Deluge Valve | PSH_003 |  |  | DI |  |  | 1 | 3 | CH14
PCS-DI.dwg | PSH_004 |  | Monitoring Signal of Pressure Switch of Tank 24 Foam Deluge Valve | PSH_004 |  |  | DI |  |  | 1 | 3 | CH15
PCS-DI.dwg | PSH_005 |  | Monitoring Signal of Pressure Switch of Tank 25 Cooling Deluge Valve | PSH_005 |  |  | DI |  |  | 1 | 3 | CH16
PCS-DI.dwg | PSH_006 |  | Monitoring Signal of Pressure Switch of Tank 25 Foam Deluge Valve | PSH_006 |  |  | DI |  |  | 1 | 3 | CH17
PCS-DI.dwg | PSH_007 |  | Monitoring Signal of Pressure Switch of Gas Boot Cooling Deluge Valve | PSH_007 |  |  | DI |  |  | 1 | 3 | CH18
PCS-DI.dwg | PSH_008 |  | Monitoring Signal of Pressure Switch of Gas Boot Cooling Deluge Valve | PSH_008 |  |  | DI |  |  | 1 | 3 | CH19
PCS-DI - Copy.dwg | SPARE_I00020 |  | SPARE | SPARE_I00020 |  |  | DI |  |  | 1 | 3 | CH20
PCS-DI-Spare NO WIRE.dwg | SPARE_I00021 |  | SPARE | SPARE_I00021 |  |  | DI |  |  | 1 | 3 | CH21
PCS-DI-Spare NO WIRE.dwg | SPARE_I00022 |  | SPARE | SPARE_I00022 |  |  | DI |  |  | 1 | 3 | CH22
PCS-DI-Spare NO WIRE.dwg | SPARE_I00023 |  | SPARE | SPARE_I00023 |  |  | DI |  |  | 1 | 3 | CH23
PCS-DI-Spare NO WIRE.dwg | SPARE_I00024 |  | SPARE | SPARE_I00024 |  |  | DI |  |  | 1 | 3 | CH24
PCS-DI-Spare NO WIRE.dwg | SPARE_I00025 |  | SPARE | SPARE_I00025 |  |  | DI |  |  | 1 | 3 | CH25
PCS-DI-Spare NO WIRE.dwg | SPARE_I00026 |  | SPARE | SPARE_I00026 |  |  | DI |  |  | 1 | 3 | CH26
PCS-DI-Spare NO WIRE.dwg | SPARE_I00027 |  | SPARE | SPARE_I00027 |  |  | DI |  |  | 1 | 3 | CH27
PCS-DI-Spare NO WIRE.dwg | SPARE_I00028 |  | SPARE | SPARE_I00028 |  |  | DI |  |  | 1 | 3 | CH28
PCS-DI-Spare NO WIRE.dwg | SPARE_I00029 |  | SPARE | SPARE_I00029 |  |  | DI |  |  | 1 | 3 | CH29
PCS-DI-Spare NO WIRE.dwg | SPARE_I00030 |  | SPARE | SPARE_I00030 |  |  | DI |  |  | 1 | 3 | CH30
PCS-DI-Spare NO WIRE.dwg | SPARE_I00031 |  | SPARE | SPARE_I00031 |  |  | DI |  |  | 1 | 3 | CH31
PCS-DI-Spare NO WIRE.dwg | SPARE_I00032 |  | SPARE | SPARE_I00032 |  |  | DI |  |  | 1 | 3 | CH32
PCS-DI-Spare NO WIRE.dwg | SPARE_I00033 |  | SPARE | SPARE_I00033 |  |  | DI |  |  | 1 | 4 | CH01
PCS-DI-Spare NO WIRE.dwg | SPARE_I00034 |  | SPARE | SPARE_I00034 |  |  | DI |  |  | 1 | 4 | CH02
PCS-DI-Spare NO WIRE.dwg | SPARE_I00035 |  | SPARE | SPARE_I00035 |  |  | DI |  |  | 1 | 4 | CH03
PCS-DI-Spare NO WIRE.dwg | SPARE_I00036 |  | SPARE | SPARE_I00036 |  |  | DI |  |  | 1 | 4 | CH04
PCS-DI-Spare NO WIRE.dwg | SPARE_I00037 |  | SPARE | SPARE_I00037 |  |  | DI |  |  | 1 | 4 | CH05
PCS-DI-Spare NO WIRE.dwg | SPARE_I00038 |  | SPARE | SPARE_I00038 |  |  | DI |  |  | 1 | 4 | CH06
PCS-DI-Spare NO WIRE.dwg | SPARE_I00039 |  | SPARE | SPARE_I00039 |  |  | DI |  |  | 1 | 4 | CH07
PCS-DI-Spare NO WIRE.dwg | SPARE_I00040 |  | SPARE | SPARE_I00040 |  |  | DI |  |  | 1 | 4 | CH08
PCS-DI-Spare NO WIRE.dwg | SPARE_I00041 |  | SPARE | SPARE_I00041 |  |  | DI |  |  | 1 | 4 | CH09
PCS-DI-Spare NO WIRE.dwg | SPARE_I00042 |  | SPARE | SPARE_I00042 |  |  | DI |  |  | 1 | 4 | CH10
PCS-DI-Spare NO WIRE.dwg | SPARE_I00043 |  | SPARE | SPARE_I00043 |  |  | DI |  |  | 1 | 4 | CH11
PCS-DI-Spare NO WIRE.dwg | SPARE_I00044 |  | SPARE | SPARE_I00044 |  |  | DI |  |  | 1 | 4 | CH12
PCS-DI-Spare NO WIRE.dwg | SPARE_I00045 |  | SPARE | SPARE_I00045 |  |  | DI |  |  | 1 | 4 | CH13
PCS-DI-Spare NO WIRE.dwg | SPARE_I00046 |  | SPARE | SPARE_I00046 |  |  | DI |  |  | 1 | 4 | CH14
PCS-DI-Spare NO WIRE.dwg | SPARE_I00047 |  | SPARE | SPARE_I00047 |  |  | DI |  |  | 1 | 4 | CH15
PCS-DI-Spare NO WIRE.dwg | SPARE_I00048 |  | SPARE | SPARE_I00048 |  |  | DI |  |  | 1 | 4 | CH16
PCS-DI-Spare NO WIRE.dwg | SPARE_I00049 |  | SPARE | SPARE_I00049 |  |  | DI |  |  | 1 | 4 | CH17
PCS-DI-Spare NO WIRE.dwg | SPARE_I00050 |  | SPARE | SPARE_I00050 |  |  | DI |  |  | 1 | 4 | CH18
PCS-DI-Spare NO WIRE.dwg | SPARE_I00051 |  | SPARE | SPARE_I00051 |  |  | DI |  |  | 1 | 4 | CH19
PCS-DI-Spare NO WIRE.dwg | SPARE_I00052 |  | SPARE | SPARE_I00052 |  |  | DI |  |  | 1 | 4 | CH20
PCS-DI-Spare NO WIRE.dwg | SPARE_I00053 |  | SPARE | SPARE_I00053 |  |  | DI |  |  | 1 | 4 | CH21
PCS-DI-Spare NO WIRE.dwg | SPARE_I00054 |  | SPARE | SPARE_I00054 |  |  | DI |  |  | 1 | 4 | CH22
PCS-DI-Spare NO WIRE.dwg | SPARE_I00055 |  | SPARE | SPARE_I00055 |  |  | DI |  |  | 1 | 4 | CH23
PCS-DI-Spare NO WIRE.dwg | SPARE_I00056 |  | SPARE | SPARE_I00056 |  |  | DI |  |  | 1 | 4 | CH24
PCS-DI-Spare NO WIRE.dwg | SPARE_I00057 |  | SPARE | SPARE_I00057 |  |  | DI |  |  | 1 | 4 | CH25
PCS-DI-Spare NO WIRE.dwg | SPARE_I00058 |  | SPARE | SPARE_I00058 |  |  | DI |  |  | 1 | 4 | CH26
PCS-DI-Spare NO WIRE.dwg | SPARE_I00059 |  | SPARE | SPARE_I00059 |  |  | DI |  |  | 1 | 4 | CH27
PCS-DI-Spare NO WIRE.dwg | SPARE_I00060 |  | SPARE | SPARE_I00060 |  |  | DI |  |  | 1 | 4 | CH28
PCS-DI-Spare NO WIRE.dwg | SPARE_I00061 |  | SPARE | SPARE_I00061 |  |  | DI |  |  | 1 | 4 | CH29
PCS-DI-Spare NO WIRE.dwg | SPARE_I00062 |  | SPARE | SPARE_I00062 |  |  | DI |  |  | 1 | 4 | CH30
PCS-DI-Spare NO WIRE.dwg | SPARE_I00063 |  | SPARE | SPARE_I00063 |  |  | DI |  |  | 1 | 4 | CH31
PCS-DI-Spare NO WIRE.dwg | SPARE_I00064 |  | SPARE | SPARE_I00064 |  |  | DI |  |  | 1 | 4 | CH32
PCS-DI-Spare NO WIRE.dwg | SPARE_I00065 |  | SPARE | SPARE_I00065 |  |  | DI |  |  | 1 | 5 | CH01
PCS-DI-Spare NO WIRE.dwg | SPARE_I00066 |  | SPARE | SPARE_I00066 |  |  | DI |  |  | 1 | 5 | CH02
PCS-DI-Spare NO WIRE.dwg | SPARE_I00067 |  | SPARE | SPARE_I00067 |  |  | DI |  |  | 1 | 5 | CH03
PCS-DI-Spare NO WIRE.dwg | SPARE_I00068 |  | SPARE | SPARE_I00068 |  |  | DI |  |  | 1 | 5 | CH04
PCS-DI-Spare NO WIRE.dwg | SPARE_I00069 |  | SPARE | SPARE_I00069 |  |  | DI |  |  | 1 | 5 | CH05
PCS-DI-Spare NO WIRE.dwg | SPARE_I00070 |  | SPARE | SPARE_I00070 |  |  | DI |  |  | 1 | 5 | CH06
PCS-DI-Spare NO WIRE.dwg | SPARE_I00071 |  | SPARE | SPARE_I00071 |  |  | DI |  |  | 1 | 5 | CH07
PCS-DI-Spare NO WIRE.dwg | SPARE_I00072 |  | SPARE | SPARE_I00072 |  |  | DI |  |  | 1 | 5 | CH08
PCS-DI-Spare NO WIRE.dwg | SPARE_I00073 |  | SPARE | SPARE_I00073 |  |  | DI |  |  | 1 | 5 | CH09
PCS-DI-Spare NO WIRE.dwg | SPARE_I00074 |  | SPARE | SPARE_I00074 |  |  | DI |  |  | 1 | 5 | CH10
PCS-DI-Spare NO WIRE.dwg | SPARE_I00075 |  | SPARE | SPARE_I00075 |  |  | DI |  |  | 1 | 5 | CH11
PCS-DI-Spare NO WIRE.dwg | SPARE_I00076 |  | SPARE | SPARE_I00076 |  |  | DI |  |  | 1 | 5 | CH12
PCS-DI-Spare NO WIRE.dwg | SPARE_I00077 |  | SPARE | SPARE_I00077 |  |  | DI |  |  | 1 | 5 | CH13
PCS-DI-Spare NO WIRE.dwg | SPARE_I00078 |  | SPARE | SPARE_I00078 |  |  | DI |  |  | 1 | 5 | CH14
PCS-DI-Spare NO WIRE.dwg | SPARE_I00079 |  | SPARE | SPARE_I00079 |  |  | DI |  |  | 1 | 5 | CH15
PCS-DI-Spare NO WIRE.dwg | SPARE_I00080 |  | SPARE | SPARE_I00080 |  |  | DI |  |  | 1 | 5 | CH16
PCS-DO-CONTACT.dwg | RS_SBG_01 |  | Site Horn Strobe for Gas | RS_SBG_01 |  |  | DO |  |  | 1 | 6 | CH01
PCS-DO-CONTACT.dwg | RS_SBF_01 |  | Site Horn Strobe for Fire | RS_SBF_01 |  |  | DO |  |  | 1 | 6 | CH02
PCS-DO-CONTACT.dwg | RS_SBG_02 |  | Site Horn Strobe for Gas | RS_SBG_02 |  |  | DO |  |  | 1 | 6 | CH03
PCS-DO-CONTACT.dwg | RS_SBF_02 |  | Site Horn Strobe for Fire | RS_SBF_02 |  |  | DO |  |  | 1 | 6 | CH04
PCS-DO-CONTACT.dwg | RS_SBG_03 |  | Site Horn Strobe for Gas | RS_SBG_03 |  |  | DO |  |  | 1 | 6 | CH05
PCS-DO-CONTACT.dwg | RS_SBF_03 |  | Site Horn Strobe for Fire | RS_SBF_03 |  |  | DO |  |  | 1 | 6 | CH06
PCS-DO-CONTACT.dwg | SV_001 |  | Activation Signal of Water_Cooling System for Tank 23 | SV_001 |  |  | DO |  |  | 1 | 6 | CH07
PCS-DO-CONTACT.dwg | SV_002 |  | Activation Signal of Foam System for Tank 23 | SV_002 |  |  | DO |  |  | 1 | 6 | CH08
PCS-DO-CONTACT.dwg | SV_003 |  | Activation Signal of Water_Cooling System for Tank 24 | SV_003 |  |  | DO |  |  | 1 | 6 | CH09
PCS-DO-CONTACT.dwg | SV_004 |  | Activation Signal of Foam System for Tank 24 | SV_004 |  |  | DO |  |  | 1 | 6 | CH10
PCS-DO-CONTACT.dwg | SV_005 |  | Activation Signal of Water_Cooling System for Tank 25 | SV_005 |  |  | DO |  |  | 1 | 6 | CH11
PCS-DO-CONTACT.dwg | SV_006 |  | Activation Signal of Foam System for Tank 25 | SV_006 |  |  | DO |  |  | 1 | 6 | CH12
PCS-DO-CONTACT.dwg | SV_007 |  | Activation Signal of Water_Cooling System for Gas Boot | SV_007 |  |  | DO |  |  | 1 | 6 | CH13
PCS-DO-CONTACT.dwg | SV_008 |  | Activation Signal of Foam System for | SV_008 |  |  | DO |  |  | 1 | 6 | CH14
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00015 |  | SPARE | SPARE_Q00015 |  |  | DO |  |  | 1 | 6 | CH15
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00016 |  | SPARE | SPARE_Q00016 |  |  | DO |  |  | 1 | 6 | CH16
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00017 |  | SPARE | SPARE_Q00017 |  |  | DO |  |  | 1 | 6 | CH17
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00018 |  | SPARE | SPARE_Q00018 |  |  | DO |  |  | 1 | 6 | CH18
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00019 |  | SPARE | SPARE_Q00019 |  |  | DO |  |  | 1 | 6 | CH19
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00020 |  | SPARE | SPARE_Q00020 |  |  | DO |  |  | 1 | 6 | CH20
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00021 |  | SPARE | SPARE_Q00021 |  |  | DO |  |  | 1 | 6 | CH21
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00022 |  | SPARE | SPARE_Q00022 |  |  | DO |  |  | 1 | 6 | CH22
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00023 |  | SPARE | SPARE_Q00023 |  |  | DO |  |  | 1 | 6 | CH23
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00024 |  | SPARE | SPARE_Q00024 |  |  | DO |  |  | 1 | 6 | CH24
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00025 |  | SPARE | SPARE_Q00025 |  |  | DO |  |  | 1 | 6 | CH25
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00026 |  | SPARE | SPARE_Q00026 |  |  | DO |  |  | 1 | 6 | CH26
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00027 |  | SPARE | SPARE_Q00027 |  |  | DO |  |  | 1 | 6 | CH27
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00028 |  | SPARE | SPARE_Q00028 |  |  | DO |  |  | 1 | 6 | CH28
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00029 |  | SPARE | SPARE_Q00029 |  |  | DO |  |  | 1 | 6 | CH29
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00030 |  | SPARE | SPARE_Q00030 |  |  | DO |  |  | 1 | 6 | CH30
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00031 |  | SPARE | SPARE_Q00031 |  |  | DO |  |  | 1 | 6 | CH31
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00032 |  | SPARE | SPARE_Q00032 |  |  | DO |  |  | 1 | 6 | CH32
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00033 |  | SPARE | SPARE_Q00033 |  |  | DO |  |  | 1 | 7 | CH01
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00034 |  | SPARE | SPARE_Q00034 |  |  | DO |  |  | 1 | 7 | CH02
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00035 |  | SPARE | SPARE_Q00035 |  |  | DO |  |  | 1 | 7 | CH03
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00036 |  | SPARE | SPARE_Q00036 |  |  | DO |  |  | 1 | 7 | CH04
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00037 |  | SPARE | SPARE_Q00037 |  |  | DO |  |  | 1 | 7 | CH05
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00038 |  | SPARE | SPARE_Q00038 |  |  | DO |  |  | 1 | 7 | CH06
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00039 |  | SPARE | SPARE_Q00039 |  |  | DO |  |  | 1 | 7 | CH07
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00040 |  | SPARE | SPARE_Q00040 |  |  | DO |  |  | 1 | 7 | CH08
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00041 |  | SPARE | SPARE_Q00041 |  |  | DO |  |  | 1 | 7 | CH09
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00042 |  | SPARE | SPARE_Q00042 |  |  | DO |  |  | 1 | 7 | CH10
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00043 |  | SPARE | SPARE_Q00043 |  |  | DO |  |  | 1 | 7 | CH11
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00044 |  | SPARE | SPARE_Q00044 |  |  | DO |  |  | 1 | 7 | CH12
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00045 |  | SPARE | SPARE_Q00045 |  |  | DO |  |  | 1 | 7 | CH13
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00046 |  | SPARE | SPARE_Q00046 |  |  | DO |  |  | 1 | 7 | CH14
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00047 |  | SPARE | SPARE_Q00047 |  |  | DO |  |  | 1 | 7 | CH15
PCS-DO-CONTACT - Copy.dwg | SPARE_Q00048 |  | SPARE | SPARE_Q00048 |  |  | DO |  |  | 1 | 7 | CH16